August 13, 2016

JJM Boiler Works

Neutralizer Condensate Kits

CBM-225 / Replacement Instructions:

1.   Use protective rubber or plastic gloves and eye protection.

- The neutralizer tube must be changed on a yearly basis minimum, for heating systems and domestic hot water systems or if pH at the outlet falls below 5.0 pH.

- Remove electrical power from the hot water heater, boiler, or furnace.

- Remove inlet and outlet piping and fittings from pH treatment tube.

- Using a flat head screw driver carefully pry open the plastic brackets at the top where they connect together.

- Remove tube from the plastic mounting brackets.

- Remove either the barb or PVC fittings for reuse.

- Clean “P” traps and drain piping.

- Use old fittings and connect to the new neutralizing tube. Remount the tube by pressing the tube into the mounting brackets using a little force which will snap the bracket arms in place. Reconnect piping and fittings. Be sure there are no leaks.

- Insure that condensate can flow without any blockage.

- Dispose of the used tube properly and obey local disposal codes.

- SDS sheet can be found on our web site.

www.jjmboilerworks.com                413-527-1893 Office